## Table 1
address | type | description | length
100 | U | Output Power phase L1 [%] | 1
101 | U | Output Power phase L2 [%] | 1
102 | U | Output Power phase L3 [%] | 1
103 | U | Battery Charge Level [%] | 1
104 | S | Input Voltage phase L1 [V] | 1
105 | S | Input Voltage phase L2 [V] | 1
106 | S | Input Voltage phase L3 [V] | 1
107 | S | UPS Temperature [C°] | 1
108 | S | Autonomy Time [minutes] | 1
109 | U | UPS Status (ASCII HEX) Please check “Status Bytes table“ below | 1
110 | S | Battery Voltage [V] | 1
111 | U | Input Frequency phase L1 [Hz] | 1
112 | U | Input Frequency phase L2 [Hz] | 1
113 | U | Input Frequency phase L3 [Hz] | 1
114 | U | Powerfail Counter | 1
115 | U | Alarm Battery Bad 1 = active; 0 = not active) | 1
116 | U | Alarm: On Battery 1 = active; 0 = not active | 1
117 | U | Alarm: Battery Low 1 = active; 0 = not active | 1
119 | U | Alarm: Over temperature 1 = active; 0 = not active | 1
120 | U | Alarm: Input Bad 1 = active; 0 = not active | 1
121 | U | Alarm: Output Bad 1 = active; 0 = not active | 1
122 | U | Alarm: Output Overload 1 = active; 0 = not active | 1
123 | U | Alarm: On Bypass 1 = active; 0 = not active | 1
124 | U | Alarm: Bypass Bad 1 = active; 0 = not active | 1
125 | U | Alarm: Output Off as requested 1 = active; 0 = not active | 1
126 | U | Alarm: UPS Off as requested 1 = active; 0 = not active | 1
127 | U | Alarm: Charger Failed 1 = active; 0 = not active | 1
128 | U | Alarm: UPS Output Off 1 = active; 0 = not active | 1
129 | U | Alarm: UPS System Off 1 = active; 0 = not active | 1
132 | U | Alarm: General fault 1 = active; 0 = not active | 1
133 | U | Alarm: Diagnose test failed 1 = active; 0 = not active | 1
134 | U | Alarm: UPS Communication lost 1 = active; 0 = not active | 1
136 | U | Alarm: Shutdown pending 1 = active; 0 = not active | 1
137 | U | Alarm: shutdown imminent 1 = active; 0 = not active | 1
138 | U | Alarm: Test in progress 1 = active; 0 = not active | 1
139 | U | Alarm: Manual Bypass Switch Closed 1 = active; 0 = not active | 1
140 | U | Output Voltage phase L1 [V] | 1
141 | U | Output Voltage phase L2 [V] | 1
142 | U | Output Voltage phase L3 [V] | 1
143 | U | Output Current phase L1 [A*10] | 1
144 | U | Output Current phase L2 [A*10] | 1
145 | U | Output Current phase L3 [A*10] | 1
152 | U | Sensormanager / SM_T_COM sensor 1 Analog value | 1
153 | U | Sensormanager / SM_T_COM sensor 2 Analog value | 1
154 | U | Sensormanager sensor 3 Analog value | 1
155 | U | Sensormanager sensor 4 Analog value | 1
156 | U | Sensormanager sensor 5 Analog value | 1
157 | U | Sensormanager sensor 6 Analog value | 1
158 | U | Sensormanager sensor 7 Analog value | 1
159 | U | Sensormanager sensor 8 Analog value | 1
160 | U | Output Power phase L1 [kW] | 1
161 | U | Output Power phase L2 [kW] | 1
162 | U | Output Power phase L3 [kW] | 1
163 | U | AUX Port 1 1 = active (high); 0 = not active (low) | 1
164 | U | AUX Port 2 1 = active (high); 0 = not active (low) | 1
165 | U | AUX Port 3 1 = active (high); 0 = not active (low) | 1
166 | U | AUX Port 4 1 = active (high); 0 = not active (low) | 1

## Table 2
address | type | description | length
(1) available only in three-phase UPS (2) available only in Trimod HE, Archimod HE (3) available only in CS141, CS141 SK (4) not available in CS141B, CS141B SK

## Table 3
address | type | description | length
13